## Protocol&Example
Address |  |  | Register Name | Type | Bit | Value |  |  | Example
Hi | Low | Dec. | [6 empty] | Register Name | Address(HEX) | Address(DEC) | Request | Reply | Type | Data | Value
0 | 0x00 | 0 | Alarms | Bitwise | - | 0x0000 - OK |  |  | Alarms | 0x00 | 0 | 01 03 00 00 00 01 84 0A | 01 03 02 00 00 B8 44 | Bitwise Int16 | 0 | OK
|  |  |  | Int16 | 0 | 0x0001 - Leakage
[5 empty] | 1 | 0x0002 - Pipe Burst
[5 empty] | 2 | 0x0004 - Reverse Flow
[5 empty] | 3 | 0x0008 - Dry
[5 empty] | 4 | 0x0010 - Critical Configuration
[5 empty] | 5 | 0x0020 - Measurement Fail |  |  | Modbus接线方法：
[5 empty] | 6 | 0x0040 - Tamper |  |  | 信号 | 线 | 注解
[5 empty] | 7 | 0x0080 – Octave Battery |  |  | Tx + | 蓝 | RS485 A端
[5 empty] | 8 | 0x0100 - Units Change |  |  | Tx - | 蓝+白 | RS485 B端
[5 empty] | 9 | 0x0200 - Watch Dog |  |  | +12/24VDC | 橙 | 模块自带电池供电，可选外接电源
[5 empty] | 10 | 0x0400 - Service Required |  |  | -12/24 VDC / 公共GND | 橙+白
[5 empty] | 11 | 0x0800 – Flow Rate Cut Off
[5 empty] | 12 | 0x1000 – Module battery |  |  | Modbus默认参数：
[5 empty] | 13 | 0x2000 – Water meter-Module communication error |  |  | 从站地址：1 | 波特率：9600
0 | 0x1-0x10 | 1--16 | AMR Serial Number | Int16 | 16 registers array [MSB][LSB] |  |  |  | 传输模式：RTU | 校验方式：偶校验
[5 empty] | [0][x][0][x][0][x]...[0][x] |  |  |  | 数据位：8位 | 停止位：1位
0 | 0x11 | 17 | RTC- week day | Int16 | Meter Date and Time |  |  | 1...7 - [0][x]
0 | 0x12 | 18 | RTC - day | Int16 |  |  |  | 1...31 - [0][x]
0 | 0x13 | 19 | RTC - month | Int16 |  |  |  | 1...12 - [0][x]
0 | 0x14 | 20 | RTC - year | Int16 |  |  |  | 14...99 - [0][x]
0 | 0x15 | 21 | RTC - hours | Int16 |  |  |  | 0...23 - [0][x]
0 | 0x16 | 22 | RTC - minutes | Int16 |  |  |  | 0...59 - [0][x]
0 | 0x17 | 23 | Volume unit | Int16 | See System Units/Resolutions table |  |  |  | Volume unit | 0x17 | 23 | 01 03 00 17 00 01 34 0E | 01 03 02 00 00 B8 44 | Int16 | 0 | m³
0 | 0x18 | 24 | Forward volume | double | Forward volume |  |  |  | Forward volume | 0x18-0x1F | 24--31 | 01 03 00 18 00 04 C4 0E | 01 03 08 66 66 66 66 66 66 08 40 EC BA | double | 3.05
0 | 0x20 | 32 | Reverse volume | double | Reverse volume |  |  |  | Reverse volume | 0x20-0x27 | 32--39 | 01 03 00 20 00 04 45 C3 | 01 03 08 7B 14 AE 47 E1 7A A4 3F 07 F5 | double | 0.04
0 | 0x28 | 40 | Volume Resolution index | Int16 | Value to multiply Forward/Reverse volume
0 | 0x29 | 41 | Current Flow | double | Current flow |  |  |  | Current Flow | 0x29-0x30 | 41--48 | 01 03 00 29 00 04 95 C1 | 01 03 08 C3 F5 28 5C 8F C2 D5 3F 3F 10 | double | 0.34
0 | 0x31 | 49 | Flow Resolution index | Int16 | Value to multiply Current flow
0 | 0x32 | 50 | Flow Units | Int16 | See System Units/Resolutions table |  |  |  | Flow Units | 0x32 | 50 | 01 03 00 32 00 01 25 C5 | 01 03 02 00 00 B8 44 | Int16 | 0 | m³/h
0 | 0x33 | 51 | Flow Direction | Int16 | See System Units/Resolutions table |  |  |  | Flow Direction | 0x33 | 51 | 01 03 00 33 00 01 74 05 | 01 03 02 00 01 79 84 | Int16 | 1 | Forward Flow
0 | 0x34 | 52 | Temperature Value | Int16 | See System Units/Resolutions table |  |  |  | Temperature Value | 0x34 | 52 | 01 03 00 34 00 01 C5 C4 | 01 03 02 00 0E 39 80 | Int16 | 15
0 | 0x35 | 53 | Temperature Unit | Int16 | See System Units/Resolutions table |  |  |  | Temperature Unit | 0x35 | 53 | 01 03 00 35 00 01 94 04 | 01 03 02 00 01 79 84 | Int16 | 1 | Celsius
0 | 0x36 | 54 | Forward volume_ui32 | Uint32 | Forward volume (int representation)
0 | 0x3A | 58 | Reverse volume_ui32 | Uint32 | Reverse volume (int representation)
0 | 0x3E | 62 | Current Flow_i32 | Int32 | Current flow (int representation)
0 | 0x42 | 66 | Signed volume | double | Signed volume
0 | 0x4A | 74 | Unsigned volume | double | Unsigned volume
0 | 0x52 | 82 | Signed volume_i32 | Int32 | Signed volume (int representation)
0 | 0x56 | 86 | Unsigned volume_ui32 | Uint32 | Unsigned volume (int representation)
| 0x5A | 90 | Pressure units | Int16 | Possible Options : |  |  |  | Pressure units | 0x5A | 90 | 01 03 00 5A 00 01 A4 19 | 01 03 02 00 00 B8 44 | Int16 | 0 | Bar,1bar=14.5Psi=100kpa=0.1Mpa
0 – Bar
1 - Psi
| 0x5B | 91 | Pressure current value | Float | Float representation |  |  |  | Pressure current value | 0x5B-0x5E | 91--94 | 01 03 00 5B 00 02 B5 D8 | 01 03 04 33 BF 19 40 CE F3 | float | 2.4
| 0x5F | 95 | Pressure Alarms | Int16 | Bit |  | Value |  | Pressure Alarms | 0x5F | 95 | 01 03 00 5F 00 01 B4 18 | 01 03 02 00 00 B8 44 | Int16 | 0 | No Alarms
[5 empty] | 0x0000 |  | No Alarms
[5 empty] | 0x1000 |  | Leakage Pressure
[5 empty] | 0x2000 |  | Burst Pressure
[5 empty] | 0x4000 |  | Communication Pressure Error
0 | 0x6F | 111 | Alarms | Bitwise | The same like register 0
Int16
0 | 0x70 | 112 | Forward volume | Uint32 | Long AB CD representation, 2 registers
0 | 0x72 | 114 | Reverse volume | Uint32 | Long AB CD representation, 2 registers
0 | 0x74 | 116 | Net Signed volume | Int32 | Long AB CD representation, 2 registers
0 | 0x76 | 118 | Signed Current Flow | Int32 | Long AB CD representation, 2 registers
0 | 0x78 | 120 | Volume Resolution index | Int16 | Value to multiply Forward/Reverse volume
0 | 0x79 | 121 | Volume unit | Int16 | See System Units/Resolutions table
0 | 0x7A | 122 | Flow Resolution index | Int16 | Value to multiply Current flow
0 | 0x7B | 123 | Flow Units | Int16 | See System Units/Resolutions table
0 | 0x7C | 124 | Temperature Value | Int16 | See System Units/Resolutions table
0 | 0x7D | 125 | Temperature Unit | Int16 | See System Units/Resolutions table
0 | 0x7E | 126 | Flow Direction | Int16 | See System Units/Resolutions table

## System Units&Resolutions
Name | Value type
Serial communication | RTU
Serial communication Parity Configuration | 0 – Even (default)
1 – Odd
2 – None
Flow Units | 0 – Cubic Meters/Hour (default)
1 – Gallons/Minute
2 – Litres/Second
3 – Imperial Gallons/ Minute
4 – Litres/Minute
5 – Barrel/Minute
Flow Resolution | [0] = 0.0001x,
[1] = 0.001x ,
[2] = 0.01x,
[3] = 0.1x,
[4] = 1x (default),
[5] = 10x,
[6] = 100x,
[7] = 1000x
[8] = 10000x
For example: if index= 3-> Flow resolution = 0.1
Volume Units | 0 – Cubic Meters (default)
1 – Cubic Feet
2 – Cubic Inch
3 – Cubic Yards
4 – US Gallons
5 – Imperial Gallons
6 – Acre Feet
7 – Kilolitres
8 – Litres
9 – Acre-Inch
10 – Barrel
Volume Resolution | [0] = 0.0001x,
[1] = 0.001x ,
[2] = 0.01x,
[3] = 0.1x,
[4] = 1x (default),
[5] = 10x,
[6] = 100x,
[7] = 1000x
[8] = 10000x
For example: if index= 3-> Volume resolution = 0.1
Flow direction | 0 - No flow
1 - Forward flow
2 - Backward flow
Temperature Units | 0 - Not Active
1 - Celsius
2 - Fahrenheit

## Example
Register Name | Address(HEX) | Address(DEC) | Request | Reply | Type | Data | Value
Alarms | 0x00 | 0 | 01 03 00 00 00 01 84 0A | 01 03 02 00 00 B8 44 | Bitwise Int16 | 0 | OK
AMR Serial Number | 0x01-0x10 | 01--16 | 01 03 00 01 00 10 15 C6 | 01 03 20 00 32 00 30 00 34 00 30 00 31 00 33 00 36 00 34 00 39 00 00 00 00 00 00 00 00 00 00 00 00 00 00 47 59 | Int16 | 204013649
Meter Date and Time | 0x11-0x16 | 17--22 | 01 03 00 11 00 06 95 CD | 01 03 0C 00 02 00 05 00 01 00 15 00 0E 00 1A 5A 93 | Int16 | 2-5-1-21-14-26 | Tue 5/1/2021 14:26
Volume unit | 0x17 | 23 | 01 03 00 17 00 01 34 0E | 01 03 02 00 00 B8 44 | Int16 | 0 | m³
Forward volume | 0x18-0x1F | 24--31 | 01 03 00 18 00 04 C4 0E | 01 03 08 66 66 66 66 66 66 08 40 EC BA | double | 3.05
Reverse volume | 0x20-0x27 | 32--39 | 01 03 00 20 00 04 45 C3 | 01 03 08 7B 14 AE 47 E1 7A A4 3F 07 F5 | double | 0.04
Volume Resolution index | 0x28 | 40 | 01 03 00 28 00 01 04 02 | 01 03 02 00 02 39 85 | Int16 | 2 | 0.01
Current Flow | 0x29-0x30 | 41--48 | 01 03 00 29 00 04 95 C1 | 01 03 08 C3 F5 28 5C 8F C2 D5 3F 3F 10 | double | 0.34
Flow Resolution index | 0x31 | 49 | 01 03 00 31 00 01 D5 C5 | 01 03 02 00 02 39 85 | Int16 | 2 | 0.01
Flow Units | 0x32 | 50 | 01 03 00 32 00 01 25 C5 | 01 03 02 00 00 B8 44 | Int16 | 0 | m³/h
Flow Direction | 0x33 | 51 | 01 03 00 33 00 01 74 05 | 01 03 02 00 01 79 84 | Int16 | 1 | Forward Flow
Temperature Value | 0x34 | 52 | 01 03 00 34 00 01 C5 C4 | 01 03 02 00 0E 39 80 | Int16 | 15
Temperature Unit | 0x35 | 53 | 01 03 00 35 00 01 94 04 | 01 03 02 00 01 79 84 | Int16 | 1 | Celsius
Forward volume_ui32 | 0x36-0x39 | 54--57 | 01 03 00 36 00 02 24 05 | 01 03 04 00 00 01 34 FA 74 | Uint32 | 308
Reverse volume_ui32 | 0x3A-0X3D | 58--61 | 01 03 00 3A 00 02 E4 06 | 01 03 04 00 00 00 04 FB F0 | Uint32 | 4
Current Flow_i32 | 0x3E-0x41 | 62--65 | 01 03 00 3E 00 02 A5 C7 | 01 03 04 00 00 00 22 7A 2A | Int32 | 34
Signed volume | 0x42-0x49 | 66--73 | 01 03 00 42 00 04 E4 1D | 01 03 08 90 C2 F5 28 5C 8F 08 40 2E 5F | double | 3.07
Unsigned volume | 0x4A-0x51 | 74--81 | 01 03 00 4A 00 04 65 DF | 01 03 08 90 C2 F5 28 5C 8F 08 40 2E 5F | double | 3.07
Signed volume_i32 | 0x52-0x55 | 82--85 | 01 03 00 52 00 02 65 DA | 01 03 04 00 00 01 33 BB B6 | Int32 | 307
Unsigned volume_ui32 | 0x56-0x59 | 86--89 | 01 03 00 56 00 02 24 1B | 01 03 04 00 00 01 34 FA 74 | Uint32 | 308
Pressure units | 0x5A | 90 | 01 03 00 5A 00 01 A4 19 | 01 03 02 00 00 B8 44 | Int16 | 0 | Bar
Pressure current value | 0x5B-0x5E | 91--94 | 01 03 00 5B 00 02 B5 D8 | 01 03 04 33 BF 19 40 CE F3 | float | 2.4
Pressure Alarms | 0x5F | 95 | 01 03 00 5F 00 01 B4 18 | 01 03 02 00 00 B8 44 | Int16 | 0 | No Alarms
| 0x60-0x6E | 96--110 | 01 03 00 60 00 0E C4 10 | 01 03 1C 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 5C A5
Alarms | 0x6F | 111 | 01 03 00 6F 00 01 B4 17 | 01 03 02 00 00 B8 44 | Bitwise Int16 | 0 | OK
Forward volume（正向累计） | 0x70-0x71 | 112--113 | 01 03 00 70 00 02 C5 D0 | 01 03 04 00 00 01 3B BA 70 | Uint32 | 315
Reverse volume（反向累计） | 0x72-0x73 | 114--115 | 01 03 00 72 00 02 64 10 | 01 03 04 00 00 00 04 FB F0 | Uint32 | 4
Net Signed volume（净累计） | 0x74-0x75 | 116--117 | 01 03 00 74 00 02 84 11 | 01 03 04 00 00 01 37 BA 75 | Int32 | 311
Signed Current Flow（瞬时量） | 0x76-0x77 | 118--119 | 01 03 00 76 00 02 25 D1 | 01 03 04 00 00 00 22 7A 2A | Int32 | 34
Volume Resolution index（累积量精度） | 0x78 | 120 | 01 03 00 78 00 01 04 13 | 01 03 02 00 02 39 85 | Int16 | 2 | 0.01
Volume unit（累积量单位） | 0x79 | 121 | 01 03 00 79 00 01 55 D3 | 01 03 02 00 00 B8 44 | Int16 | 0 | m³
Flow Resolution index（流量精度） | 0x7A | 122 | 01 03 00 7A 00 01 A5 D3 | 01 03 02 00 02 39 85 | Int16 | 2 | 0.01
Flow Units（流量单位） | 0x7B | 123 | 01 03 00 7B 00 01 F4 13 | 01 03 02 00 00 B8 44 | Int16 | 0 | m³/h
Temperature Value | 0x7C | 124 | 01 03 00 7C 00 01 45 D2 | 01 03 02 00 0E 39 80 | Int16 | 15
Temperature Unit | 0x7D | 125 | 01 03 00 7D 00 01 14 12 | 01 03 02 00 01 79 84 | Int16 | 1 | Celsius
Flow Direction | 0x7E | 126 | 01 03 00 7E 00 01 E4 12 | 01 03 02 00 01 79 84 | Int16 | 1 | Forward Flow